Leviton Manufacturing Co., Inc.

59-25 Little Neck Parkway

Little Neck, NY 11362-2591

Phone: 1-800-824-3005

Fax: 1-800-832-9538

[Specifier Notes:

This product specification specifies occupancy sensor lighting controls intended for indoor use. Leviton’s Occupancy Sensor (OSSMT) should meet all specifications herein. Include Leviton Manufacturing Co. as either sole manufacturer or in list of manufacturers.

Revise product specification section number and title below to suit project requirements, spec-ification practices, and section content. Optional text is contained within brackets [ ]. Use or delete bracket-enclosed optional text in the final copy of the specification, as well as all brackets. Italicized Specifier Notes typically precede corresponding text. Delete these Notes in final copy of specification.]

SECTION 13800

Building Automation and control

occupancy sensor lighting Controls

- GENERAL

  - SUMMARY

    - Section includes OSSMT multi-technology sensor.

- Self-contained wall switch with multi-technology: OSSMT-MD

    - Related Sections: Section(s) related to this section include:

      - Division 16, Lighting Accessories, Lighting Restoration and Repair Sections.

      - Division 16, Wiring Methods, Wiring Devices Section.

      - Division 16, Wiring Methods, Special Purpose Lighting.

      - Division 13, Special Lighting Control.

  - SYSTEM DESCRIPTION

    - Performance Requirements: Provide occupancy sensor lighting controls that have been manufactured, assembled, and installed to maintain performance criteria stated by manufacturer without defects, damage, or failure.

    - Performance Testing Requirements

      - Manufacturer shall 100% test all equipment prior to shipment. Sample testing is not acceptable.

    - Code Requirements

      - All occupancy sensor lighting controls shall be UL listed and either CSA or CUL/US listed.

      - All sensors shall be FCC compliant where applicable.

      - All sensors shall be California Title 24 compliant.

      - Building Codes: All units shall comply with applicable, local building codes.

  - SUBMITTALS

    - General: Submit listed submittals in accordance with Conditions of the Contract and Division 1 Submittal Procedures Section.

    - Bill of Materials: Complete list of all parts needed to fully install selected occupancy sensors.

    - Product Data: Submit product data, including catalog cut sheets for specified products.

    - Shop and Wiring Drawings: Submit shop drawings detailing all mechanical and electrical equipment including one-line diagrams, wire counts, coverage patterns, and physical dimensions of each item.

    - Fixture Compatibility: List of ballasts types and lamp combinations compatible with occupancy sensors.

    - Samples: Submit samples for finish, color, and texture.

    - Installation Instructions: Manufacturer’s installation instructions.

    - Maintenance Instructions: To remove dust and grime, wipe down units with damp cloth and mild detergent solution. Do not touch the surface of the lens.

    - Closeout Submittals: Warranty documents specified herein.

  - QUALITY ASSURANCE

    - Installer Qualifications: Installer shall be one who is experienced in performing the work of this section, and who has specialized in installation of work similar to that required for this project.

    - Source Limitations: To assure compatibility, obtain occupancy sensors from a single source with complete responsibility over all lighting controls, including accessory products. The use of subcontracted component assemblers is not acceptable.

    - Manufacturer Requirements: The manufacturer will be one who has been continuously engaged in the manufacture of commercial lighting controls and occupancy sensors for no less than 10 years.

    - ISO Certification: Manufacturer shall be ISO-9001 certified.

  - DELIVERY, STORAGE & HANDLING

    - General: Comply with Division 1 Product Requirements Sections.

    - Ordering: Comply with manufacturer’s ordering instructions and lead-time requirements to avoid construction delays.

    - Delivery: Deliver materials in manufacturer’s original, unopened, undamaged packages with intact identification labels.

[Specifier Note: Coordinate article below with Environmental Specifications section.]

    - Storage and Protection: Store materials away from exposure to harmful weather conditions and at temperature and humidity conditions recommended by manufacturer.

[Specifier Note: Coordinate article below with Conditions of the Contract and with Division 1 Closeout Submittals (Warranty) Section.]

  - WARRANTY

    - Manufacturer’s Warranty: All equipment shall be warranted free of defects in materials and workmanship.

      - Warranty Period: Five years from date of purchase.

      - Owner Rights: Manufacturer’s warranty is in addition to, not a limitation of, other rights the Owner may have under contract documents.

- PRODUCTS
[Specifier Notes: An X within a catalog number, e.g., OSSMT-MDX, stands for a variable letter or number, e.g., OSSMT-MDW or OSSMT-MDI, and is used within this specification to represent a specific type of sensor with a number of variations. An X in catalog number is a variable for the color of the device. Suffixes are as follows: ivory (-I), white (-W), almond (-A), light gray (–T) and gray (-G).]

  - Self-contained units

    - General to Wall Switches with Multi-Technology: OSSMT-MD

      - Shall use passive infrared (PIR) and ultrasonic (US) motion detection.

      - Shall use PIR to initially detect motion and turn on lights. Either PIR and/or US shall be used to keep lights on while occupied.

      - Shall be compatible with incandescent, magnetic or electronic low voltage, and magnetic or electronic fluorescent, as well as motor loads.

      - Switch shall be microprocessor controlled with Auto-Adapting learning process that automatically adjusts sensitivity and time delay based on occupancy patterns.

      - Shall be capable of detecting occupancy with true, 180º field of view.

      - Shall utilize zero crossing circuitry, which increases relay life, protects from the effects of inrush current, and increases sensor longevity.

      - Wall switch shall have integral shutters that narrow the field of view from 180º.

      - Shall feature pushbutton for manual on and off, which times out based upon occupancy detection.

      - A tri-colored LED shall indicate occupancy status for PIR (red), US (green), and US sensitivity level (yellow).

      - US sensitivity (High, Medium and Low) shall be user adjustable by a press and hold function of the ON-OFF button.

      - Manual PIR range, photocell, and time settings shall be user-configurable.

      - Switch shall be rated at 120/277V in one unit.

      - Unit shall fit in a standard box and use a standard wallplate, which is gangable.

      - Wall switch shall not protrude more than .4 inches from box.

      - Shall be a Decora style unit with a matching wallplate available.

      - Wall switch must be available in white, ivory, light almond, almond, and gray.

    - OSSMT-MD

      - Shall use microprocessor for motion signal analysis and internal, adaptive self-adjustment.

      - No manual adjustment shall be required at the time of installation or during operation.

      - Shall automatically adapt to changing room conditions—including background PIR levels and continuous airflow.

      - Shall save learned and adjusted settings in non-volatile memory that retains all settings during power outages.

      - Shall recognize motion detected within 20 seconds of turning off lighting as a false off. In response to a false off, the microprocessor shall increase the time-off setting.

      - Maximum adapted time-out shall not exceed 30 minutes.

      - Shall operate in 40 kHz ultrasonic frequencies.

      - Walk through feature shall shut off lights within 2.5 minutes after momentary occupancy.

      - Four, selectable manual timer settings shall be available from 30sec to 30min.

      - Rating: 1200W/VA @ 120V, 2700VA @ 277V, and 1/4HP @ 120VAC

- EXECUTION

  - PREPARATION

    - Site Verification: Verify that wiring conditions, which have been previously installed under other sections or at a previous time, are acceptable for product installation in accordance with manufacturer’s instructions.

    - Inspection: Inspect all material included in this contract prior to installation. Manufacturer shall be notified of unacceptable material prior to installation.

[Specifier Note: Coordinate article below with manufacturer’s recommended installation details and requirements.]

  - INSTALLATION

    - The Electrical Contractor, as part of the work of this section, shall coordinate, receive, mount, connect, and place into operation all equipment. The Electrical Contractor shall furnish all conduit, wire, connectors, hardware, and other incidental items necessary for properly functioning lighting control and occupancy sensors as described herein and shown on the plans. The Electrical Contractor shall maintain performance criteria stated by manufacturer without defects, damage, or failure.

      - Compliance: Contractor shall comply with manufacturer’s product data, including shop drawings, technical bulletins, product catalog installation instructions, and product carton instructions for installation.

    - Power: The contractor shall test that all branch load circuits are operational before connecting loads to sensor system load terminals, and then de-energize all circuits before installation.

    - Related Product Installation: Refer to other sections listed in Related Sections for related products’ installation.

  - TESTING

    - Upon completion of all line, load and interconnection wiring, and after all fixtures are installed and lamped, a qualified factory representative shall completely check the installation prior to energizing the system. Each installed occupancy sensor shall be tested in the test mode to see that lights turn off and on based on occupancy.

    - At the time of checkout and testing, the owner’s representative shall be thoroughly instructed in the proper operation of the system.

  - PROTECTION

    - Contractor shall protect installed product and finished surfaces from damage during all phases of installation including preparation, testing, and cleanup.

END OF SECTION