# Engineering Specifications

# Leviton 4100 Series

# Bi-Directional Compact Power and Energy Meter

# with BACnet Communication

- The power meter shall be fully electronic with multi-line backlit LCD display showing measured parameters as well as alarm functions and pulse output.

- The power meter shall perform the following measurements:

- Total Real Energy (kWh) (a signed net sum of all energy imported and exported)

- Real Energy (kWh), imported (from the grid), exported (to the grid) for each phase and totals for all phases

- Reactive Energy (kVARh), both imported (from the grid) and exported (to the grid), by Quadrant, as defined by IEEE 1459-2000

- Apparent Energy (kVAh), imported (from the grid), exported (to the grid), and signed net total

- Net Present Demand for Real (kW), Reactive (kVAR) and Apparent (kVA) Power over a user-specified interval (block or sliding window)

- Maximum (Peak) Real (kW), Reactive (kVAR) and Apparent (kVA) Demand Intervals, both imported (from the grid) and exported (to the grid)

- Instantaneous Real (kW), Reactive (kVAR) and Apparent Power (kVA), by phase and in total

- Current (amps) for each phase and average of all phases

- Phase-to-phase voltage for each phase and average of all phase pairs

- Phase-to-neutral voltage for each phase pair and average of all phases

- Power factor for each phase and average of all phases

- AC frequency

- The power meter shall communicate using the BACnet MS/TP protocol at speeds from 9600 to 115,200 baud (no parity).  The meter shall provide a BACnet Device object, a set of  writeable Analog Value objects for remote configuration, a set of Analog Input objects to provide access to scaled 32-bit measurement values and their unit types, and a set of Binary Input objects for indicating individual alarm conditions.

- The meter shall be UL/CUL listed to the latest applicable safety standards.

- Power meter models must be available to directly accept voltage input over the range of 90 to 600 VAC (50 or 60Hz).

- The power meter shall accept either 0 to 0.333VAC or 0 to 1VAC input from up to three current transducers to 32000 amps.

- The measured energy consumption shall be retained in non-volatile memory for the life of the product warranty.

- The power meter shall have demand measurement programmable for up to 6 sub-intervals of 10 seconds to 546 minutes duration.

- Meter shall be optionally available in an outdoor NEMA 4X enclosure.

- The power meter shall operate from -30C to +70C.

- The power meter shall have dimensions not exceeding 4.2” x 3.6” x 2.3”.

- The power meter shall be Leviton S4100 or equivalent.

- The power meter shall meet both ANSI C12.20 .2% and IEC 62053-22 Class .2S real power and energy accuracy specifications.

- The power meter shall meet IEC 62053-22 Class 2 reactive power and energy accuracy specifications.

- The power meter shall be configurable for operation on Single Phase (AN or AB), Split Phase (ABN), Delta (ABC), and Wye (ABCN) systems.

- The power meter shall have separate control power inputs such that is may be powered from a different service than it measures.

- The power meter shall have Phase Loss Alarm contacts with a user configurable phase loss threshold.

- The power meter shall have a user-configurable Pulse Contact input to support measurement of other related energy (Gas, Water, Steam, etc.) via BACnet using a simple pulse-output transducer.

- The power meter shall be configurable for use with Potential Transformers to 32000 volts.

- The power meter shall support warnings for low power factor (phase current or voltage miss-wired), current over range, voltage over range, and frequency out of range.

- The product shall have a 5-year warranty.