Leviton Manufacturing Co., Inc.
201 N Service Rd
Melville, NY 11747-3138
Phone: 1.800.323.8290
Fax: 1.800.832.9538

SECTION 16570

CENTRAL DIMMING CONTROLS

Leviton a-2000 Dimmer Panels

This specification is dated May 5, 2011. It replaces any and all previous a-2000 specifications.

This document can and should be edited to suit project requirements. Editing notes are included as HIDDEN TEXT. They can be revealed or hidden by one of the following methods:

To display hidden text in Word 2010 documents: Click the File tab. The Backstage view appears. Under Help, click Options. The Options dialog appears. Click Display and select Hidden Text.

To print hidden text in Word 2010 documents: Click the Microsoft Word button. Then click the Word tab. Then click the Options button. The Word Options dialog opens. Click the Display tab in the left pane. Check the Print hidden text checkbox under Printing Options in the right pane of the Word Options dialog.

In older versions of Microsoft Word: From the pull-down menus select TOOLS, then OPTIONS. Under the tab labeled VIEW, select or deselect the HIDDEN TEXT option.

To print a copy of the specification that includes the HIDDEN TEXT, (1) Select “Print” (2) Select “Options” (3a) Check the box to print HIDDEN TEXT (3b) Uncheck the box to not print HIDDEN TEXT.

NOTE TO SPECIFIER: This product specification section specifies dimmer panels with a software interface that can integrate with daylight sensors, 0 — 10 VDC analog controllers, and networked control systems operating on the LumaNet or DMX512 protocols. Leviton’s a-2000 Dimmer Panels meet all specifications herein. Include Leviton Manufacturing Co. Inc. as either sole manufacturer or in list of manufacturers.

Revise product specification section number and title to suit project requirements, specification practices, and section content.

While using this specification, take note of the following:

Hypertext links are included to those organizations whose standards are referenced within the text, to assist in product selection and further research.

Optional text requiring a selection by the user is enclosed within brackets, e.g.: “Section [09000.] [_____.]"

Items requiring user input are enclosed within brackets, e.g.: “Section [_____ - ________]."

Optional paragraphs are separated by an "OR" statement: you will see the following line between these paragraphs:

**** EITHER ****

Option A

**** OR ****

Option B

# GENERAL

## RELATED DOCUMENTS

### Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 specification Sections.

### All contract documents and addenda.

NOTE TO SPECIFIER: a-2000 panels are programmed from the front panel for control by external analog or digitally networked devices. Options include Leviton’s Dimensions D4200  and D8000 LumaNet control networks, or the DMX512 protocol, or 0 — 10 VDC analog signals. Any network controllers or external analog controllers used on your project will be specified in this section. Leviton publishes complete system specifications for the Dimensions D4200  / a-2000 and D8000 / a-2000 combinations, with both CSI Masterformat 2004 and 1995 section numbering.

## SUMMARY

### Section Includes:

#### Central dimming control panel[s].

### Related Sections:

NOTE TO SPECIFIER: Edit the following paragraphs to coordinate with other sections in the Project Manual. a-2000 dimmer panels are optionally available from the factory with an attached relay panel.

#### Section [13845 – Relay Lighting Controls:] Switching panels.

#### Section [16140 - Wiring Devices/Lighting Controls.]

#### Section [16580 - Ballasts:] Fluorescent lighting ballasts controlled by Dimming Control System.

### Contractor responsibilities:

#### Coordinate, receive, mount, connect, and place into operation all equipment. Furnish all conduit, wire, connectors, hardware, and other incidental items necessary for the complete and properly functioning relay lighting control system as described herein and shown on the plans.

## REFERENCES

NOTE TO SPECIFIER: Standards that are not referenced elsewhere in this Section are not a required part of Article 1.3. They can be deleted.

### American National Standards Institute/Institute of Electrical and Electronic Engineers (ANSI/IEEE) (www.ansi.org and www.ieee.org)

#### C62.41-1991 — Recommended Practice for Surge Voltages in Low-Voltage AC Power Circuits.

### [ASTM International (ASTM) (www.astm.org)

#### D4674 -02a Standard Test Method for Accelerated Testing for Color Stability of Plastics Exposed to Indoor Fluorescent Lighting and Window-Filtered Daylight.]

### Canadian Standards Association (CSA) (www.csa.ca).

#### CSA C22.2 # 14 Industrial Control Equipment

#### CSA C22.2 # 184 Solid-State Lighting Controls

#### CSA C22.2 # 156 Solid-State Speed Controls

### International Electrotechnical Commission (www.iec.ch).

#### (IEC) 801-2 Electrostatic Discharge Testing Standard.

#### IEC/EN 60669-2-1 Switches for household and similar fixed electrical installations - electronic switches.

### International Organization for Standardization (ISO) (www.iso.ch):

#### 9001:2000 — Quality Management Systems.

### [National Electrical Manufacturers Association (NEMA) (www.nema.org)

#### WD1 (R2005) - General Color Requirements for Wiring Devices.]

### National Fire Protection Association (NFPA) (www.nfpa.org)

#### NFPA 70: National Electrical Code (NEC), Article 100

### Norma Official Mexicana (NOM).

#### NOM-003-SCFI Productos eléctricos - Especificaciones de seguridad (Electrical products - Safety Specifications)

#### 489 (2002) - Molded-Case Circuit Breakers, Molded-Case Switches, and Circuit-Breaker Enclosures.

NOTE TO SPECIFIER: UL 508 is an important safety standard that Underwriters Laboratories uses to independently evaluate, test and List Industrial Control Equipment, including dimmer panels. UL 508 listed products will fail safely in the event that the output terminals to the load are short-circuited.

#### 508 (1999) - Standard for Industrial Control Equipment.

NOTE TO SPECIFIER: UL 1472 is the Underwriters Laboratories Standard for Safety of Solid State Dimming Controls. It defines limits on the amount of DC voltage a dimmer can deliver to a magnetic ballast or transformer.

#### 1472 (1996) - Solid-State Dimming Controls.

NOTE TO SPECIFIER: UL 924 is the UL Standard for Safety for Emergency Lighting and Power Equipment. It ensures that the lighting system will meet safety requirements in emergency situations.

#### 924 (2003) - Emergency Lighting and Power Equipment

NOTE TO SPECIFIER: ASHRAE 90.1 specifies that qualifying products withstand voltage surges of up to 6000V and 3000V as described in ANSI/IEEE C63.41-1980

### American Society of Heating, Refrigerating and Air-Conditioning (ASHRAE)

#### ASHRAE 90.1

### California Energy Commission (CEC)

#### Title 24

## SUBMITTALS

NOTE TO SPECIFIER: Edit the following to coordinate with other sections in the Project Manual.

#### Submit under provisions of Section [01330] and in accordance with Conditions of the Contract.

### Bill of Materials: Complete list of all parts needed to fully install selected system components.

### Specification Conformance Document: Indicate whether the submitted equipment:

#### Meets specification exactly as stated.

#### Meets specification via an alternate means and indicate the specific methodology used.

***OR***

### Product Certificates: Signed by manufacturers of equipment certifying that products furnished comply with specified requirements.

### Shop Drawings

#### To be prepared by competent draftspersons specifically for this project

##### Generic drawings are not acceptable.

#### Submit for approval within 30 days following receipt of contract

##### Approval is required prior to equipment fabrication

#### Detail all mechanical and electrical equipment, including:

##### Load schedule indicating:

###### For each circuit:

            - actual connected load

            - load type

            - voltage

            - capacity

            - phase

###### Circuit numbers and their respective control zones

###### Circuits having emergency priority.

##### Separate system wiring riser diagrams for each and every system showing each major item of equipment and connections.

##### Device termination diagrams

##### System programming information including zones and schedules.

##### Sound data including results of operational tests of central dimming controls.

### Product Data: Product data sheets with performance specifications demonstrating compliance with specified requirements.

### Installation Instructions: Manufacturer’s installation instructions.

### Field Test Reports: Indicate and interpret test results for tests specified in Part 3.

### Maintenance Data

#### Include record of Owner’s equipment-programming option decisions.

## Closeout Submittals

### To be provided within two weeks following system turn-on.

#### Warranty documents specified herein.

#### Three sets of operation and maintenance manuals.

#### Two complete sets of as-built drawings

## QUALITY ASSURANCE

NOTE TO SPECIFIER: Edit the following to indicate the minimum level of experience required by architectural lighting control manufacturers.

NOTE TO SPECIFIER: The following applies to all components covered herein.

### Manufacturer Requirements

#### Continuously engaged in the manufacture of architectural lighting controls and relays for no less than ten years.

#### Provide factory-direct technical support hotline 24 hours per day, 7 days per week.

#### Maintain a quality system that is registered to the ISO 9001:2000 Quality Standard.

### Central dimming control system components:

#### Listed by [CE] [CSA] [NOM] [UL] specifically for the required loads, or certified by recognized independent testing organizations that test to [CE] [CSA] [NOM] [UL] standards.

#### Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction.

NOTE TO SPECIFIER: The following paragraphs ensure that the system will withstand surges generated by most lightning strikes, and that all user accessible points such as terminal blocks, buttons, and control inputs have effective protection against Electrostatic Discharges (ESD). ESD tests follow the human body model described in the IEC 801-2 standard.

#### Comply with ASHRAE 90.1

#### Comply with CEC Title 24

#### Designed and tested to withstand electrostatic discharges up to 15,000 V without damage or memory loss per IEC 801-2.

#### Designed and tested to withstand voltage surges up to 6000V and current surges up to 3000A per ANSI/IEEE standard 62.41-1980

### Installer Qualifications

#### Experienced in performing the work of this section

#### Has specialized in installation of work similar to that required for this project.

NOTE TO SPECIFIER: Paragraph E below assures continued effective service and warranty support for the Owner.

### Source Limitations

#### To assure compatibility, obtain all system components from a single source with complete responsibility for all lighting controls and accessories specified in this Section, in Division 13 Section “Lighting Controls,” and in Division 16 Section “Relay Lighting Controls.” The use of subcontracted component assemblers is not acceptable.

## products installed but not furnished under this section

NOTE TO SPECIFIER: Fluorescent ballasts can use different technologies for dimming, including 0 — 10 VDC, two-wire (power and control on the same wire pair) and three-wire (dimmed and switched AC power wires, plus neutral). Dimmer modules must be configured for the specific ballast type they are controlling: otherwise the ballast can be damaged.

### Ballasts

#### Any fluorescent ballasts supplied to be compatible with the equipment being furnished on this project.

NOTE TO SPECIFIER: For maximum lamp life, lamp manufacturers recommend their fluorescent lamps should be operated at full brightness for a minimum or 100 hours before dimming is permitted. For best results, lamp brands and types should not be intermixed on a circuit

### All conduit, wire, connectors, hardware, and other incidental items necessary for the complete and properly functioning central dimming control systems described herein and shown on the plans.

NOTE TO SPECIFIER: Use of Leviton-approved wire for all digital low voltage wiring runs is required. We strongly recommend Belden 9829, Belden 8102, Belden 1502R or Belden 9729 for Luma-Net® wire runs.

## DELIVERY, STORAGE & HANDLING

### General: Comply with Division 1 Product Requirements Sections.

### Ordering: Comply with manufacturer’s ordering instructions and lead-time requirements to avoid construction delays.

### Delivery

#### Deliver materials in manufacturer’s original, unopened, undamaged packages with intact identification labels.

#### Deliver to other trades in a timely manner.

NOTE TO SPECIFIER: Coordinate Article below with Environmental Specifications sections.

### Storage and Protection: Store materials away from exposure to harmful weather conditions and at temperature and humidity conditions recommended by manufacturer.

NOTE TO SPECIFIER: Coordinate Article below with Conditions of the Contract and with Division 1 Closeout Submittals (Warranty) Section.

## PROJECT CONDITIONS

### Do not install equipment until the following conditions can be maintained in spaces to receive equipment:

#### Ambient temperature: 0° to 40° C (32° to 104° F).

#### Relative humidity: Maximum 90 percent, non-condensing.

#### Lighting control system must be protected from dust during installation.

## WARRANTY

### Manufacturer’s Warranty

#### Warrant all equipment free of defects in materials and workmanship.

#### Warranty Period

##### Warrant all system components for 25 months from date of shipment, or two years from date of turn-on, whichever occurs first.

##### Make extended warranties available.

#### Owner’s Rights: Manufacturer’s warranty is in addition to, not a limitation of, other rights the Owner may have under contract documents.

## COMMISSIONING

As specified in Article 1.11, a lighting control system requires at least one site visit for proper commissioning. If multiple site visits are required, the first ensures that the contractor is trained to install the system correctly. On the second, the factory engineer will start up the system, ensure that it is operating according to specification, and perform initial programming. The third visit is for the purposes of refining the programming, and training the owner/end user on the system.

NOTE TO SPECIFIER: Delete the commissioning option you DO NOT want in this specification.

### Provide factory-certified field service engineer to ensure proper system installation and operation under following parameters:

#### Certified by the equipment manufacturer on the system installed.

*** EITHER ***

#### Site visit activities:

##### Verify connection of power feeds and load circuits.

##### Verify connection of controls.

##### Verify system operation control by control, circuit by circuit.

##### Obtain sign-off on system functions.

##### Demonstrate system capabilities, operation and maintenance and educate Owner’s representative on the foregoing.

*** OR ***

#### At least three site visits to accomplish the following tasks:

##### Prior to wiring

###### Review and provide installer with instructions to correct any errors in the following areas:

            - Low voltage wiring requirements

            - Separation of high and low voltage wiring runs

            - Wire labeling

            - Load schedule information

            - Switching cabinet locations and installation

            - Physical locations and network addresses of controls

            - Ethernet connectivity

            - Computer-to-network connections

            - Load circuit wiring

            - Connections to other systems and equipment

            - Placement and adjustment of Photocells

##### After system installation

###### Check and approve or provide correction instructions on the following:

            - Connections of power feeds and load circuits

            - Connections and locations of controls

            - Connections of low voltage inputs

            - Connections of the data network

###### Turn on system control processor and upload any pre-programmed system configuration

###### Verify cabinet address(es)

###### Upload pre-programmed system configuration and information to switching and/or dimming cabinets

###### Check load currents and remove bypass jumpers

###### Verify that each system control is operating to specification

###### Verify that each system circuit is operational according to specification

###### Verify that manufacturers’ interfacing equipment is operating to specification

###### Verify that any computers and software supplied by the manufacturer are performing to specifications

###### Verify that any remote WAN (Wide Area Network) connections are operating properly

###### Have an owner’s representative sign off on the above-listed system functions

##### Before project completion and hand-off

###### Demonstrate system capabilities and functions to owner’s representative

###### Train owner’s representative on the proper operation, adjustment, and maintenance of the system.

### Notification: Upon completion of the installation, the contractor shall notify the manufacturer that the system is ready for formal checkout. Notification shall be given in writing a minimum of 21 days prior to the time factory-trained personnel are required on site. Each field installed RJ45 connection must be tested prior to system interconnection. A test report must be furnished to manufacturer prior to scheduling commissioning activity. Manufacturer shall have the option to waive formal turn-on.

### Turn-On: Upon completion of all line, load and interconnection wiring, and after all fixtures are installed and lamped, Manufacturer’s Certified Technician shall completely check the installation prior to energizing the system. Each installed relay system shall be tested for proper ON/OFF operations, and proper LED illumination. Each installed control cabinet shall be tested verifying that each controlled load adjusts to the selected setting and that all switch LED’s illuminate properly.

### At the time of checkout and testing, the owner’s representative shall be thoroughly instructed in the proper operation of the system.

## MAINTENANCE

### Enable the end user to order new equipment for system expansion, replacements, and spare parts.

### Make new replacement parts available for a minimum of ten years from the date of manufacture.

As specified in Article 1.12, Paragraph C, Leviton Manufacturing provides telephone technical support by factory personnel 24 hours a day, 7 days a week. Project cost overruns and delays can occur without this service. Answering services can add to frustration and delay the resolution of any problems or issues. Manufacturers who do not offer factory-direct technical support on a 24/7 basis should not be acceptable on this project.

### Provide factory-direct technical support hotline 24 hours per day, 7 days per week.

### Offer renewable annual service contracts, to include parts, factory labor, and annual training visits. Make service contracts available up to ten years after date of system commissioning.

# PRODUCTS

## MANUFACTURERS

*** EITHER ***

### Acceptable Manufacturer: Leviton Manufacturing Co. Inc. — System: Leviton a-2000 Dimmer Panel[s]

****OR****

### Basis of design product: Leviton Manufacturing Co. Inc. a-2000 Dimmer Panel[s] or subject to compliance and prior approval with specified requirements of this section, one of the following:

#### Leviton Manufacturing Co. Inc. a-2000 Dimmer Panel[s]

#### <<To specify an alternate manufacturer and product, insert their names here. Otherwise, delete this entire line.>>

### Substitutions: [Not permitted.] [Permitted.]

Note to Specifier: Delete items 1 through 4 if substitutions are not permitted.

#### Show all substitutions as an add or deduct from the base bid price

##### All substitutions subject to provisions of [Section 00 26 00] [Section 01 25 00] [Section 01 62 00] [Division 1]

#### Clearly delineate all proposed substitutions as such and submit in writing for approval by the design professional a minimum of 10 working days prior to the bid date.

##### Proposed substitutions must be made available to all bidders.

##### Proposed substitutes must be accompanied by a review of the specification noting compliance on a line-by-line basis.

#### Prior to rough-in, provide complete engineered shop drawings, including power wiring, with deviations from the original design highlighted in an alternate color, to the engineer for review and approval.

#### By using pre-approved substitutions, the contractor accepts responsibility and associated costs for all required modifications to circuitry, devices, and wiring.

## GENERAL

### Dimming Performance Requirements

- NOTE TO SPECIFIER: Dimming equipment is typically rated for 40°C (104°F): the maximum ambient temperature that should exist while the dimming equipment is operating at full load. The following statement ensures that the system is designed to operate in worst-case environmental conditions without diminished product life.

#### Design dimmers to operate continuously in ambient temperatures ranging from 0° C (32°F) to 40° C (104°F) with up to 90 percent non-condensing relative humidity.

#### All dimming electronics to employ Silicon Controlled Rectifiers (SCRs)

- NOTE TO SPECIFIER: When in the Off state, the semiconductor in a dimmer circuit can allow current leakage to the load, which can result in an electrical shock. It is common for this leakage current to exceed the UL limit for a GFCI outlet (5 milliamps). A physical disconnect in the Off state eliminates current leakage and prevent electric shock when servicing the load.

#### Provide a means to disconnect the load from line supply when user needs to service the load.

- NOTE TO SPECIFIER: When power is restored after a dropout, the lighting system should recover quickly and should automatically return to the same illumination levels that existed before the dropout.

#### Return lights to previously set levels when power is restored following an interruption.

- NOTE TO SPECIFIER: Improperly designed products provide stepped, not continuous, lighting control.

#### Control all light sources in a smooth and continuous fashion without visible steps.

- NOTE TO SPECIFIER: The following paragraph is intended to minimize inrush, extend lamp life, and provide a better user experience.

##### Smoothly change illumination levels to programmed settings within 350µs.

NOTE TO SPECIFIER: Lighting sources such as fluorescent and incandescent lamps operate within different power ranges from minimum to maximum. Dimmers with too narrow a control range will not provide the full range of illumination levels. Dimmers with too broad a control range will overshoot some light sources: changing the dimmer’s output level will not produce any change in illumination. Dimmers must be flexible enough to compensate for these different load types. Lighting loads and circuits frequently change as projects develop.  The following statement ensures that the specified product can adapt to load and circuit changes without replacing the panel.

##### Each dimmer rated to 20A continuous operation

As specified in Article 2.2, Paragraph 6.c, Leviton’s a-2000 dimmer modules include a “Universal” module that can be configured in the field for almost any load type. This allows the contractor to adapt the system to the actual load types during installation and gives the designer greater flexibility in using different types of lighting. Systems that lack this degree of versatility and flexibility can result in higher costs for the Owner, and should not be acceptable on this project.

##### Each dimmer slot to have assignable, field-configurable load types with corresponding dimming curves and ranges.

###### Incandescent

###### Quartz

###### Quartz halogen

###### Tungsten Argon

###### Magnetic Low Voltage

###### Electronic Low Voltage

            - Subject to dimmer manufacturer evaluation

###### Low power factor neon and cold cathode transformers

###### Two-Wire Fluorescent Ballasts

###### Three Wire Fluorescent Ballasts

- NOTE TO SPECIFIER: Variations among lamp and fixture designs may require fine-tuning the dimming curves. The following statement ensures that the system allows these adjustments. This statement also allows facility personnel to manage illumination levels in accordance with energy savings goals and plans.

##### Each dimmer to have programmable minimum and maximum light levels.

##### Each dimmer to have a programmable cutoff level.

## [Leviton a-2000 Series] DIMMER PANEL[S]

NOTE TO SPECIFIER: Edit the following: include all dimmer panel and/or rack systems that will be included in this system.  Delete all that are not included in the system.

### General

As specified in Article 2.3, Paragraph A.2, Leviton a-2000 dimmer panels are designed for easy installation and / or replacement of dimmer modules. No wiring is required. Shipping screws or blanking plate screws may have to be removed, but in many situation the module simply slides in and out and locks in place mechanically. The panel recognizes the type of dimmer module automatically based on physical characteristics. Dimmer panels that require re-wiring when replacing or installing dimmer modules are costly and labor-intensive to install and maintain, and should not be acceptable on this project.

NOTE TO SPECIFIER: Standalone a-2000 panels are available with 12-module or 24-module capacity. 36-module and 48-module panels can be assembled at the factory (but not in the field) by attaching either one 12-module and one 24-module panel, or two 24-module panels. Delete options below that are not part of your project.

#### Capacity

##### [12] [24] dimmer modules

##### [36] [48] dimmer modules

###### Factory-configured

As specified in Article 2.3, Paragraph 1.c, a-2000 Series dimmer panels are designed with modular plug-in dimmers that can be installed and / or replaced in the field without re-wiring. This allows the contractor to accommodate design changes at any stage of the construction process, and gives the designer greater freedom to adapt the system to client needs. Costs of these changes are minimized by the ease and speed of dimmer module replacement. Systems with hard-wired dimmers will impose substantial costs if Owner requirements mandate changing the system after it has been delivered, and should not be acceptable on this project. Operating and maintenance costs will also be lower than older technologies that require multiple wire terminations, since modules can be removed and replaced without the need to call a factory technician or a specialized electronics repair technician.

##### Enable dimmer module installation and replacement without re-wiring

###### Hard-wired dimmer modules are not acceptable

#### Accept the following control signals:

##### LumaNet III

##### DMX512

##### 0 — 10 VDC analog

###### Via optional analog control card

#### Automatically recognize and support the following dimmer module types:

##### Dual Dimmer Module

##### Constant Module

##### High Rise-Time Module

##### Dual Universal Module

### Physical:

#### NEMA Type 1 indoor enclosure

#### 14 gauge steel

#### Mount in standard stud walls, fitting between two standard stud spacings

#### Surface mountable

##### When surface mounted, meet ADA (Americans With Disabilities Act) requirements

As specified in Article 2.3, Paragraph B.5, a-2000 dimmer cabinets can be flush mounted to save space in the electrical rooms with tight mounting clearances. The slim profile of the cabinet combined with the flush mounting capability can aid in meeting code requirements for clearance space between the cabinet surface and wall opposite. Dimmer cabinets that cannot be flush mounted may require larger, more costly electrical rooms in order to meet code requirements, and should not be acceptable on this project.

#### Flush mountable with optional flush mount trim kit

### Electrical:

NOTE TO SPECIFIER: 230 V a-2000 panels require a three-phase power input; 120 V and 277 V panels can be wired for either single-phase or three-phase AC power.

#### Main input power: [120 VAC] [227 VAC] [single phase] [three phase] [220 — 240 VAC] [three phase]

NOTE TO SPECIFIER: a-2000 dimmer panels are available with attached, fully pre-wired relay cabinets: these must be attached at the Leviton factory. The primary application of these relay cabinets is 277V fluorescent dimming with a 0 — 10 VDC analog control signal. Relay cabinets can also accommodate any 120V or 347V switched (non-dimming) load. They may be configured with branch circuit breakers. Delete the following text if your project does not use the factory-configured, attached relay cabinets.

#### [Manufacturer to supply dimmer panel(s) with attached, factory-configured relay cabinet(s)]

##### [277V] [120V] relays as detailed in the drawings]

##### [Branch circuit breakers as detailed in the drawings]

##### Branch circuit breakers; meet following performance requirements:

###### Listed to UL 489 as molded case circuit breaker for use on lighting circuits.

###### Rated at 10,000 AIC.

###### UL listed as switch duty (SWD) so that loads can be switched on and off by breakers.

#### Available with main circuit breakers or main lugs

##### Main lugs sized to allow every dimmer module to be loaded to maximum capacity

NOTE TO SPECIFIER: 12-circuit a-2000 panels supply 10 Amps of +24 VDC; 24-circuit panels supply 6 Amps. The number of control stations that can be powered directly from the dimmer panel depends on the “unit loads” of 25 mA per unit consumed by each control station, on the length of the wire run and the gauge of the wire (wires cause voltage to drop over distance, and thinner wires cause more of a voltage drop because their resistance per unit of length is higher). The manufacturer’s instructions explain how to calculate the appropriate wiring and powering needs for a specific project. Leviton Manufacturing maintains an Applications Engineering department that can manage these calculations for your project.

#### Supply + 24 VDC power to networked control stations

#### Provide eight (8) 0 — 10 VDC analog output channels

### Digital control electronics

#### Functions

##### Display system operating status

##### Identify errors and malfunctions

##### Configure dimmer modules

##### Assign network addresses to dimmer modules

As specified in Article 2.3, Paragraph D.2, a-2000 dimmer panels can be completely programmed and controlled from the full-function, multi-line LCD display on the front panel. The LCD display allows easy access to all system functions, enabling Owner’s personnel to program the system and/or modify settings without the need for a factory technician with specialized knowledge of function codes, or an external computer for programming and uploading configuration files. Systems without this level of operational integrity should not be acceptable on this project.

#### Front Panel LCD display

##### Display software version, main feed status and phase unless Function buttons are engaged

#### Function Buttons

##### Full Bright

###### Push once to override all assigned dimmers to full brightness

###### Push twice to release and return dimmers to external control

###### Dimmers can be assigned to respond to external Full Bright commands for emergency functions

##### Select / Save

###### Display incoming voltage and frequency of all AC power phases on LCD

##### Cancel / Clear

###### Display software version, main feed status and phase on LCD

#### LED Indicators

##### Phase Loss: indicates low voltage or loss on any phase of the main feed

##### Full Bright: indicates that the panel is operating in Full Bright mode

##### FAN: indicates that power is present at the fan motor(s)

##### AUX, DMX, LUMANET: indicate control signals are being received by blinking

#### Navigation buttons

##### Up, Down, Left, Right

### Panel Control Software

#### Programmable from front panel LCD, Navigation, Select / Save and Cancel / Clear buttons

#### Assign LumaNet and / or DMX512 channels to dimmer modules

#### Configure features common to all dimmer types:

##### Full Bright Input: Toggles On/Off override to Full Bright from the front panel

##### External Full Bright: Toggles On/Off override to Full Bright from an external contact.

###### Assignable to any network channel

###### [Assignable to maximum of 4 network groups]

##### Control input source:

###### Scan All (A)

###### EXT Full Bright

###### Full Bright

###### Analog

###### Luma-Net

###### DMX512

##### DMX 512 Address: Sets the DMX address for that particular circuit (1 — 512)

##### Luma-Net Address: Sets the Luma-Net address for that particular circuit (1 — 2048)

##### Dimmer Feedback for Luma-Net on or off.

##### Max and Min Levels

##### Assign analog input

###### If applicable

##### Assign Photocell

#### Dimmer configurations

##### Curve

###### Square Law

###### Linear Voltage

###### Linear Lights

##### Cutoff level for specific load types:

###### Non-Dim

###### Mark X (10)

###### Mark VII (7)

###### Low Voltage Magnetic

###### Lutron Tu-Wire™

###### HiLume™

##### Associate with one of (8) 0-10VDC low voltage control outputs

###### Control ballasts that require a 0-10VDC control signal (Mark VII or similar) without requiring an additional external interface

## [leviton a-2000 dimmer modules

### Module Types

#### Dual Dimmer Module [Leviton p/n’s 000-A20DD -012(120V) & -A27 (120/277V)]

#### Constant Module [Leviton p/n’s 000-A20DC -012 (120V) & -A27 (120/277V)]

##### No switching or dimming: circuit breaker only

NOTE: At certain brightness levels, rapid heating and cooling of incandescent filaments can cause an objectionable buzzing noise. As specified in Article 2.4, Paragraph A.3, a-2000 dimmer modules can include “high rise time” (700 µs) filter chokes designed to minimize noise when controlling incandescent lamps. Dimmer panels without this capability should not be acceptable on this project.

#### High Rise-Time Module [Leviton p/n 000-A20HD-012]

        - High (700 µs) rise time dimmers occupy a full module space when used for incandescent loads

As specified in Article 2.4, Paragraph 4, a-2000 systems include a “universal” module that can control all dimmable load types typically found in commercial construction projects. This eliminates the need to coordinate load types with dimmer ratings and greatly simplifies the specification, coordination, and installation process. Load types can be identified in the field and the dimmer simply programmed to control them. Systems without this level of adaptability and flexibility will increase project complexiy and Owner’s costs, and should not be acceptable on this project.

#### Dual Universal Module [Leviton p/n’s 000-A20UN-012(120V), -027 (120/277V)]

##### Programmable for the following load types:

###### DM: suitable for incandescent lamps, quartz halogen lamps, stepdown transformers for low voltage incandescent lamps, and neon or cold cathode low power factor type transformers

###### M7: suitable for dimming ballasts requiring that the 120 V power be turned on and off, and controlled by a 0 — 10 V signal

            - Maximum capacity of 100 ballasts per circuit

###### TU: suitable for Lutron TuWire dimming ballasts

###### MX: suitable for Advance Mark X dimming ballasts

###### ND: switched On/Off operation

###### LV: suitable for low-voltage stepdown transformers and other loads that require a low-end cutoff

            - Subject to dimmer manufacturer evaluation: transformer must incorporate thermal protection or have a fused primary winding.

###### HL: suitable for Lutron HiLume and Eco-10™ dimming ballasts

As specified in Article 2.4, Paragraph B, a-2000 dimmer modules include bypass switches that allow loads to be operated at full output without engaging the dimmer’s control capability. Bypassing the dimmer circuitry is especially useful during construction, installation and maintenance. Unlike mechanical bypass jumpers that can be hard to find when needed, and difficult to install when found, built-in switches make it easy to bypass the dimmer control circuitry whenever this function is needed. Systems without bypass switches should not be acceptable on this project.

### Bypass switches

#### Non-Universal Modules

##### 120V: Bypass switch removes all dimming electronics from the circuit

##### 277V: Bypass accomplished by optional constant shunt module

#### Universal Module

##### Normal mode: Red LED unlit; SCR’s and relays operated by control module

##### Bypass mode: Red LED illuminated; SCR’s and relays are forced On

## COMPONENTS

### A-2000 Series Panels

#### 12 Circuit

#### 120V single-phase, standard [Leviton LMS p/n A2D1L-112]

#### 120V single-phase, standard w/analog input [Leviton LMS p/n A2B1L-112]

#### 120V 3-phase, standard [Leviton LMS p/n A2D3L-112]

#### 120V 3-phase, standard w/analog input [Leviton LMS p/n A2B3L-112]

#### 277V single-phase, standard [Leviton LMS p/n A2D1L-212]

#### 277V single-phase, standard w/analog input [Leviton LMS p/n A2B1L-212]

#### 277V 3-phase, standard [Leviton LMS p/n A2D3L-212]

#### 277V 3-phase, standard w/analog input [Leviton LMS p/n A2B3L-212]

#### 24 Circuit

#### 120V single-phase, standard [Leviton LMS p/n A2D1L-124]

#### 120V single-phase, standard w/analog input [Leviton LMS p/n A2B1L-124]

#### 120V 3-phase, standard [Leviton LMS p/n A2D3L-124]

#### 120V 3-phase, standard w/analog input [Leviton LMS p/n A2B3L-124]

#### 277V single-phase, standard [Leviton LMS p/n A2D1L-224]

#### 277V single-phase, standard w/analog input [Leviton LMS p/n A2B1L-224]

#### 277V 3-phase, standard [Leviton LMS p/n A2D3L-224]

#### 277V 3-phase, standard w/analog input [Leviton LMS p/n A2B3L-224]

#### 36 Circuit

#### 120V single-phase, standard [Leviton LMS p/n A2D1L-136]

#### 120V single-phase, standard w/analog input [Leviton LMS p/n A2B1L-136]

#### 120V 3-phase, standard [Leviton LMS p/n A2D3L-136]

#### 120V 3-phase, standard w/analog input [Leviton LMS p/n A2B3L-136]

#### 277V single-phase, standard [Leviton LMS p/n A2D1L-236]

#### 277V single-phase, standard w/analog input [Leviton LMS p/n A2B1L-236]

#### 277V 3-phase, standard [Leviton LMS p/n A2D3L-236]

#### 277V 3-phase, standard w/analog input [Leviton LMS p/n A2B3L-236]

#### 48 Circuit

#### 120V single-phase, standard [Leviton LMS p/n A2D1L-148]

#### 120V single-phase, standard w/analog input [Leviton LMS p/n A2B1L-148]

#### 120V 3-phase, standard [Leviton LMS p/n A2D3L-148]

#### 120V 3-phase, standard w/analog input [Leviton LMS p/n A2B3L-148]

#### 277V single-phase, standard [Leviton LMS p/n A2D1L-248]

#### 277V single-phase, standard w/analog input [Leviton LMS p/n A2B1L-248]

#### 277V 3-phase, standard [Leviton LMS p/n A2D3L-248]

#### 277V 3-phase, standard w/analog input [Leviton LMS p/n A2B3L-248]

#### Main Circuit Breakers (factory installation required: single cabinets only)

#### Single phase 120/240V cabinets

- Indicate breaker size in amps (for example A2K1B-30 is a 30 amp main breaker).

#### A2K1B – [30] [50] [60] [70] [80] [100] [125] [150] [175] [200] [225]

#### 3-phase 120/240V cabinets

#### A2K3B – [30] [50] [60] [70] [80] [100] [125] [150] [175] [200] [225]

#### 3-phase 277/480V cabinets

- 150 amps and larger breakers are available only for 24-circuit cabinets

#### A273B – [30] [50] [60] [70] [80] [100] [125] [150] [175] [200]

### Dimmer Modules

#### a-2000 Series

##### 120V/20A Universal Dual Dimmer Module [Leviton LMS p/n A20UN-012]

##### 120/277V/20A Universal Dual Dimmer Module [Leviton LMS p/n A20UN-027]

##### 120V/20A Dual Dimmer Module [Leviton LMS p/n A20DD-012]

##### 120V/20A Dual Constant Module [Leviton LMS p/n A20DC-012]

##### 120V/20A High Rise Dimmer Module [Leviton LMS p/n A20HD-012]

##### 277V/20A Dual Dimmer Module [Leviton LMS p/n A20DD-A27]

##### 277V/20A Dual Constant Module [Leviton LMS p/n A20DC-A27]

##### 240V/15A Dual Dimmer Module [Leviton LMS p/n A15DD-230]

##### 240V/20A Dual Dimmer Module [Leviton LMS p/n A20DD-230]

# EXECUTION

## INSTALLATION

### Coordinate, receive, mount, connect, and [place into operation] all equipment.

### Install equipment in accordance with manufacturer’s installation instructions.

#### Install relay panels in locations where audible noise is acceptable.

#### Use only with 75° C (167° F) copper wire at 75% ampacity.

### Provide complete installation of system in accordance with Contract Documents.

### Maintain performance criteria stated by the manufacturer without defects, damage, or failure.

### Provide equipment at locations and in quantities indicated on Drawings

#### Provide any additional equipment required to provide control intent.

As specified in Article 3.1, Paragraph F, interior sensors work mainly with diffused light and have a much higher lighting gain than exterior sensors. Electric light sources can affect these sensors unless the sensors are shielded from the light given off by electric light sources.

### Ensure that daylight sensor placement minimizes sensors view of electric light sources; ceiling mounted and fixture-mounted daylight sensors shall not have direct view of luminaries.

NOTE TO SPECIFIER: Contractor places equipment into operation unless factory commissioning is specified.

### Furnish all conduit, wire, connectors, hardware, and other incidental items necessary for a properly functioning lighting control and relay system as described herein and shown on the plans. The Electrical Contractor shall maintain performance criteria stated by the manufacturer without defects, damage, or failure.

NOTE TO SPECIFIER: The following three tables apply specifically to Leviton Manufacturing’s a-2000 dimmer panels: delete if substitutions are allowed.

#### Size dimmer panel main feed wires according to the following table:

| Cabinets with Factory-Installed Main Breakers |  |  |
| --- | --- | --- |
| Main Breaker Size (A) | Cabinet Sizes | Wire Size |
| 30, 50, 60 | 12, 24 | #14-#2 AWG |
| 40 | 24 | #14-#2 AWG |
| 70, 80, 100 | 12, 24 | #12-2/0 AWG |
| 90 | 24 | #12-2/0 AWG |
| 110, 125 | 24 | #4-250kcmil |
| 125 (1 phase only) | 12 | #4-250kcmil |
| 150 | 24, 36 | #4-250kcmil |
| 175, 200 | 24, 36 | #4-250kcmil |
| 225 | 36 | #4-250kcmil |
| Main Breaker not available | 48 | N/A |

| Cabinets with Main Lugs |  |  |  |
| --- | --- | --- | --- |
| Cabinet Size | Phase | Max Feed Size | Wire Size |
| 12 | 1 | 125A | #14-#2 AWG |
|  | 3 | 80A | #14-#2 AWG |
| 24 | 1 | 250A | #6-250kcmil |
|  | 3 | 250A | #6-250kcmil |
| 36 | 1 | 250A | #4 - 250kcmil |
|  | 3 | 175A | #4 - 250kcmil |
| 48 | 1 | 500A (2) | #6-250kcmil |
|  | 3 | 350A (2) | #6-250kcmil |

#### Size dimmer panel load circuit wires according to the following table:

| Load Terminal |  | Neutral Block |  |
| --- | --- | --- | --- |
| Quantity | Size (AWG) | Quantity | Size (AWG) |
| 1 | #8 | 1 | #4 |
| 1 | #10 | 1 | #6 |
| 1-3 | #12 | 1 | #8 |
| 1-4 | #14 | 1 | #10 |
|  |  | 1 | #12 |
|  |  | 1 | #14 |

### Comply with manufacturer’s product data, including shop drawings, technical bulletins, product catalog installation instructions, and product carton instructions for installation.

### Test that all branch load circuits are operational before connecting loads to system load terminals, and then de-energize all circuits before installation.

### DO NOT apply power to the dimming system during construction and prior to turn-on unless specifically authorized by written instructions from the manufacturer.

NOTE TO SPECIFIER: Delete the following item if factory commissioning is required. If the contractor should include switch programming as part of the installation, delete any switch types that are not included in the project (if both analog low-voltage and digital switches are included, you will delete all brackets in the following item).

### [Programming: Program [low-voltage] [and] [digital switch] functionality at the control panel.]

### Furnish information as to the exact brand, type, and model number of the fluorescent dimming ballasts being used in the fixtures on this project to the dimming manufacturer.

#### Failure to inform dimmer manufacturer terminates all responsibility for system compatibility with the ballasts on job site.

### Wire networks with 2000 feet (600 meters) total run length: verify run lengths prior to installation.

#### No splices. No exceptions.

#### Provide field installation reports verifying that cable installations are operational and compliant with standard.

### Notify the Lighting Control System Supplier that the system is ready for testing.

#### Provide notification a minimum of thirty (30) days prior to the date for testing.

## SITE VERIFICATION

### Verify that wiring conditions, which have been previously installed under other sections or at a previous time, are acceptable for product installation in accordance with manufacturer’s instructions.

## FIELD MEASUREMENTS

### Take field measurements

### Coordinate the physical size of all equipment with the architectural requirements of the spaces into which they are to be installed.

## INSPECTION

### Inspect all material included in this contract prior to installation.

### Notify Manufacturer of unacceptable material prior to installation.

## SITE PROTECTION

### Contractor shall protect installed product and finished surfaces from damage during all phases of installation including storage, preparation, testing, and cleanup.

### Provide factory-direct technical support hotline 24 hours per day, 7 days per week.

### Offer renewable annual service contracts, to include parts, factory labor, and annual training visits. Make service contracts available up to ten years after date of system commissioning.

END OF SECTION