## Dimming System

### General Description

1.  The rack shall contain 24 dimmer module slots for housing up to 48 dimmers.

2.  The rack shall offer an option for a redundant control module that provides seamless backup in case of the main control module’s failure or removal from the rack.

- Each dimmer module shall monitor the temperature parameters for each dimmer.

### Dimmer Rack Mechanical

1.  The rack is built from extruded aluminum structural members with removable side panels of code gauge steel, measuring 50” high x 17” wide x 24” deep.

2.  All exterior surfaces shall be finished in textured black powder coat finish.

3.  Side, rear, top and bottom panels shall be easily removed without dismantling the rack.

4.  Since the racks require no rear or side access, racks shall be able to be mounted back-to-back or side-to-side.

5.  The front of the rack shall be completely open, allowing clear installer access to all line, load and control terminations.

6.  Dedicated wire guides shall be mounted internally to aid in installation of load circuit wiring.  Each load termination shall accept up to a #2 AWG wire.

7.  The cooling fan and its control unit shall be mounted in removable modular housings for easy cleaning and maintenance.

8.  Each dimmer shall receive fresh air through the door-mounted electrostatic filter.

9.  Each rack shall have a locking door.

10. All dimmers shall be housed in removable modules made of die cast aluminum.

11. Each module shall contain one or two circuit breakers, a solid-state power switching device (SSR), a dimmer control PCB assembly, and two filter chokes.

12. All electrical contacts shall feature self-aligning floating connectors to insure precise alignment of all connections.

13. Modules shall be keyed so that a module of higher ampacity cannot be inserted into a slot that is wired for a lower ampacity dimmer.

- All dimmer modules shall be inserted and removed without the use of any tools.

### Dimmer Rack Mechanical

1.  The rack shall be designed to operate on voltages ranging from 90-135VAC (120V nominal) at 50/60  Hz.

2.  Rack shall be for use with four-wire three-phase or single-phase power.  Simple rack-to-rack bussing eliminates the need to run separate line feeds to each rack.

3.  The rack shall be UL listed and C-UL listed (for Canadian applications) with a short-circuit current rating of 100,000 RMS amps symmetrical  providing listed dimmer modules are installed and the racks are not modified.

4.  Optional current-limiting fault-current fuses (Amp-Traps) shall be available for other 100, 000 short-circuit current applications.

5.   In systems that require a ground wire per load circuit, an optional ground bus shall be installed inside the rack.

6.  All bussing, and all line and load terminal shall be copper.

### Control Module

1.  Each rack shall contain an electronic backplane with all control wiring connections on removable screw terminals for easy control wiring.

2.  The backplane shall also retain all rack configurations, analog scenes, and backup scenes or looks in non-volatile memory, so that when any new control module is inserted, it automatically comes on-line, fully functional within ten seconds without requiring any programming by the user.

3.  Each rack shall require a single control module that connects to the rack’s electronic backplane.

4.  Control modules shall be inserted and removed without the use of any tools.

5.  Multiple control module outputs shall automatically pile-on to each other in a “highest takes precedence” fashion.

6.  Each control module shall have three LED’s to indicate the presence of voltage on each power phase.

7.  The control module shall also contain LED’s for overtemp, active control sources, panic and diagnostics.

8.  The rack configuration and all backup scenes shall be able to be accessed through Hand-Held Terminal plugged into the front of the module, or remotely.

9.  The 120V control module shall be UL Listed and C-UL Listed.

10. Each control module has an opto-isolated DMX512 input, a twelve-scene analog input and a 99-scene backup input.  The module combines all inputs in a “highest takes precedence” manner.  Analog scenes include snapshot capability.

11. Each dimmer shall be able to be programmed for the following operating parameters:

a) Minimum and maximum level

b) Non-dim operation

c) Softpatch

12. Feedback information shall appear through the LED’s of each dimmer module.

13. Feedback information to the control module for each dimmer shall include overtemp warning.

14. In addition to feedback from each dimmer, the rack shall monitor and provide feedback for the active voltage per phase.

16. Each rack comes with hardware-selectable Panic operation.

17. Terminals for dry contact closures shall be provided to initiate a Panic scene which shall drive all selected dimmers without affecting any other control setting.

### Dimmer Module General

1.  The dimmer module shall be designed for superior reliability in the most demanding of operating conditions.

- 2. Each dimmer module shall monitors it’s temperature and report this information to the control module.

- 3. Each dimmer module shall have a dedicated optically isolated control signal line from the control module.

- 4. The failure of one module shall not affect the operation of any other dimmer module.

### Dimmer Module Mechanical

- 1.  All dimmers shall be housed in removable modules made of die-cast aluminum.

- 2.  Each module shall contain one or two circuit breakers, a solid-state power switching device (SSR), a dimmer control PCB assembly, and two filter chokes.

- 3.  The face of the module shall have a handle, the circuit breaker switches, air vents, and labeled LEDs for local feedback.

- 4.  The left side of the module shall have a wide section of spring steel to insure a proper fit for each module in the rack.

- 5.  All electrical contacts shall feature self-aligning floating connectors to insure precise alignment of all connections.

- 6.  Modules shall be keyed so that a module of higher ampacity cannot be inserted into a slot that is wired for a lower ampacity dimmer.

- 7.  All dimmer modules shall be inserted and removed without the use of any tools.

### Dimmer Module Electrical

- 1.  The dimmer module shall  designed to operate on voltages ranging from 90-135VAC (120V nominal) at 50/60 +/-1Hz.

- 2.  The load lugs in the rack shall be capable of accepting up to #2 AWG wire.

- 3.  The dimmer module electronics’ firing signal shall be optically isolated to 4,000 Volts from the power semiconductors.

- 4.  The control signal from the control console shall be optically isolated from the control module electronics.

- 5. The dimmer module shall be capable of withstanding the following adverse conditions without any interruption of operation:

- a) A complete dropout of line voltage for up to 10 milliseconds

- b) A line surge or sag of 25% of nominal operating voltage for at least 500 	milliseconds

- c) Transient voltages up to 21/2 times the nominal line voltage

- 6.  The module shall also maintain proper output voltage regulation with +/- 1 
Volt for line voltage changes of up to 10% per second, and for line frequency changes of up to 1 Hertz per second.

- 7.  Each dimmer shall be able to be programmed for the following operating parameters:

- a) Soft patch

- b) Minimum and maximum level

- c) Non-dim operation

- 8.  When a dimmer is set as a non-dim, it shall pass a full sine wave unregulated from the input voltage.

- 9.   Each dimmer shall track overtemp and level conditions, and provides feedback to the LEDs on the face of the dimmer module.

- 10.   Real-time feedback information to the control module for each dimmer shall include:

- a) Over-temperature warning

- b) Over-temperature shutdown.

- 11.  Modules shall be available in standard (500microsecond) rise times measured from 10% to 90% at 90 degrees conduction angle under full load. Oscillographic evidence of rise time data shall be provided before approval of any alternated manufacturer is allowed.

- 12.  Airflow modules shall be required in unused slots in order to maintain proper rack ventilation.

- 13.  120V units shall be UL listed and C-UL listed (for Canadian applications).

- 14.   Dimensions:		   		H			W			D

- Dual & Single Modules		11/2”  3.8cm		121/2”  31.8cm      61/2”  16.5cm

- 15. i Series e Dimmer Modules Rise Time and Maximum Heat Loss Per Channel

- Catalog#	Description		    Rise Time   Current Rating        Max Heat Loss Per Channel

- (in Microseconds)                  Watts     BTU/hr     Ton/AC

- __________________________________________________________________________________________

- 4-0011E	i500 1.8KW 120V Dual Dimmer Module	500       2 x 15A	       	 70	     239          .020

- 4-0012E	i500 2.4KW 120V Dual Dimmer Module	500       2 x 20A       	 93	     317          .027

- 4-0014E	i500 6.0KW 120V Single Dimmer Module	500	    50A	      	 264 	     900          .076

- 4-0061E	i500 2.5KW 230V Dual Dimmer Module         500      2 x 15A	      	 119            406	       .034

- 4-0052E	i350 5.0KW 230V Dual Dimmer Module         350      2 x 25A	        	   96            327          .028

- 4-0064E	i500 5.0KW 230V Single Dimmer Module  	500            25A	     	 224            764          .064

- 4-0031         i Series 15Amp 120V Constant Module                2 x 20A

Provide the following:

Qty.    Catalog No. 	Description

#	4-0122E	i48e Rack: 120V Standard Dual 1.8/2.4kW., Sequential

#	4-0301	Hand Held Terminal

#	4-0311E	Control Module 120V

#	4-0011E	i500e  1.8KW Dual Dimmer Module

#	4-0012E	i500e  2.4KW Dual Dimmer Module

#	4-0014E	i500e  6.0KW Single Dimmer Module

#	4-0099	i Series Air Flow Module

#	7-4041	Hand-Held Terminal Wall Receptacle